## WB! Status
What'sBest!® 8.0.4.4 (Aug 23, 2006) - Library 4.1.1.93 - Status Report -
DATE GENERATED: | 2008-02-22 22:17 | 39500.9285
MODEL INFORMATION:
CLASSIFICATION DATA Current Capacity Limits
--------------------------------------------------------
Numerics 46
Variables 44
Adjustables 8 500
Constraints 15 250
Integers/Binaries 0/4 50
Nonlinears 10 50
Coefficients 89
Minimum coefficient value: 0.06119 on Costs!D13
Minimum coefficient in formula: Costs!D14
Maximum coefficient value: 25000 on <RHS>
Maximum coefficient in formula: Costs!B22
MODEL TYPE: Mixed Integer / Nonlinear
SOLUTION STATUS: LOCALLY OPTIMAL
OPTIMALITY CONDITION: SATISFIED
OBJECTIVE VALUE: 2129.5146330126
DIRECTION: Minimize
SOLVER TYPE: Branch-and-Bound
TRIES: 188
INFEASIBILITY: 9.9999999747524e-007
BEST OBJECTIVE BOUND: 2129.5146330126
STEPS: 1
ACTIVE: 0
SOLUTION TIME: 0 Hours 0 Minutes 3 Seconds
NON-DEFAULT SETTINGS:
General Options / Warning Nonlinearity Present: Off
End of Report

## Costs
Process Energy Dispatch Optimization
|  |  | Predicted |  |  |  | INPUTS
NATURAL GAS
LSU NG Price Delivered (HHV) |  |  | 7.781 | $/MMBTU |  |  | Campus Electricity Demand |  |  | 25000 | kW
NG Purchased (HHV) |  |  | 235.1476 | MMBTU/hr |  |  | Campus Steam Demand |  |  | 100 | mlb/hr
Natural Gas (HHV) |  |  | 1054.8677 | BTU/SCF
NG flow rate (based on NG_HHV) |  |  | 222.9167 | mSCF/hr
NG Cost |  |  | 1829.6836 | $/hr
VARIABLE ELECTRICITY
Rate |  |  | 0.06119 | $/kW-hr
Electricity Purchased |  |  | 4900 | kW
Electricity Cost |  |  | 299.831
TOTAL COST |  |  | 2129.5146 | $/hr
ELECTRICITY BALANCE | [5 empty] | STEAM BALANCE
PRODUCED (kW) |  |  | USED (kW) |  |  | PRODUCED (mlb/hr) |  |  | USED (mlb/hr)
GE Gas Turbine | 20100 |  | Campus | 25000 |  | Boiler 8 | 89.5535 |  | Campus | 100
Imported | 4900 |  |  |  |  | Boiler 8 Supp. | 10.4465
SUM | 25000 |  | SUM | 25000
[6 empty] | Boiler 4 | 0 |  | SUM | 100
[6 empty] | SUM | 100
NATURAL GAS
[6 empty] | PURCHASED (MMBTU/hr) |  |  | USED (MMBTU/hr)
[6 empty] | SUM | 235.1476 |  | GE Gas Turbine | 224.3845
[9 empty] | Boiler 8 Supp. | 10.7631
[9 empty] | Boiler 4 | 0
[9 empty] | SUM | 235.1476
EQUIPMENT SELECTION
NAME | ON/OFF | IN |  | OUT |  | EFFICIENCY |  | MAX CAPACITY |  | MIN CAPACITY
Boiler 4 | 0 | 34.5854 | MMBTU/hr | 29.5572 | mlb/hr | 85.9145 | % | 100 | mlb/hr | 20 | mlb/hr
GE GasTurbine | 1 | 224.3845 | MMBTU/hr | 20100 | kW | 30.5654 | % | 20100 | kW | 4000 | kW
Boiler 8 | 1 | 224.3845 | MMBTU/hr | 89.5535 | mlb/hr | 40.2578 | % | 89.57 | mlb/hr | 36.2 | mlb/hr
Boiler 8 Supp. | 1 | 10.7631 | MMBTU/hr | 10.4465 | mlb/hr | 97.9025 | % | 60.43 | mlb/hr | 0 | mlb/hr
CONSTRAINTS for use in What's Best Solution
NAME |  |  | CONSTRAINT
GE Gas Turbine = Boiler 8 binary |  |  | #VALUE!
GE Gas Turbine = Boiler 8 mcf/hr |  |  | #VALUE!
Boiler 8 Supp <= Boiler 8 binary |  |  | #VALUE!
Electricity Imported >= 0 |  |  | #VALUE!
Electricity Produced = Consumed |  |  | #VALUE!
Steam Produced = Consumed |  |  | #VALUE!
Natural Gas Purchased = Used |  |  | #VALUE!
Equipment Capacity |  |  | MAX | MIN
| Boiler 4 |  | #VALUE! | #VALUE!
| GE Gas Turbine |  | #VALUE! | #VALUE!
| Boiler 8 |  | #VALUE! | #VALUE!
| Boiler 8 Supp. |  | #VALUE! | #VALUE!