## Sheet1
Coal Combustion Analysis
MW C | 12 |  | MW Air | 28.84 |  | MW CO2 | 44 | kg_to_lb | 2.2046
MW H | 1 |  | MW O2 | 32 |  | MW SO2 | 64
MW O | 16 |  | MW N2 | 28
MW S | 32 |  | MW H2O | 18
MW N | 14
| Elemental Coal Analysis (wt%) |  |  | Air Analyis (mole %)
C | 63.75 |  |  | N2 | 79 |  |  |  |  | Excess Air | 1.2 | Conesville #5 (also see down the column for OUT mass flows)
H | 4.5 |  |  | O2 | 21 | [5 empty] | 0.2
O | 6.88 | [10 empty] | Consistency Check IN
N | 1.25 |  |  | Ex 14.1 |  | Ex 14.2 | IN | OUT GAS | Boiler | OUT GAS | Boiler | DOE Conesville #5
S | 2.51 | [7 empty] | Exit with |  | Exit with | Adjusted Basis
Ash | 9.99 |  |  |  |  | In |  |  | Theoretical |  | 1.2 x
Water | 11.12 |  |  |  |  | Assume 1000g Coal/s |  |  | Air |  | Air
Sum | 100 |  |  | g Air/g Coal Element |  |  | Grams/s |  | Moles/s |  | Moles/s |  | lb/hr | DOE Report
|  |  | C: | 11.4444 |  | C | 637.5 | CO2 | 53.125 | CO2 | 53.125 | C | 238715.0625 | 236665
|  |  | H: | 34.3333 |  | H | 45 | H2O | 22.5 | H2O | 22.5 | H | 16850.475 | 16102
|  |  | O: | -4.2917 |  | O | 68.8 | O2 (fuel+air) | none | O2 (fuel+air) | 12.6019 | O | 25762.504 | 26566
|  |  | N: | none |  | N | 12.5 | N2(fuel+air) | 237.4817 | N2(fuel+air) | 284.8888 | N | 4680.6875 | 4868
|  |  | S: | 4.2917 |  | S | 25.1 | SO2 | 0.78438 | SO2 | 0.78438 | S | 9398.8205 | 10110
|  |  | Ash: | none |  | Ash | 99.9 | Ash | none | Ash | none | Ash | 37408.0545 | 42313
|  |  | Water: | none |  | Water | 111.2 | Water | 6.1778 | Water | 6.1778 | Water | 41639.396 | 37820
|  |  | Total | 8.6533 |  | Total (g/s) | 1000 | Total (mol/s) | 320.0688 | Total (mol/s) | 380.0778 | Total (g/s) | 374455 | 374455 | Raw Coal
[9 empty] | As |  | As
[9 empty] | ppm |  | ppm
|  | consistency checks |  |  |  | consistency check |  | CO2 | 165979.9138 | CO2 | 139774.0229
| 237.0353 |  | N2 | 6636.9875 |  | air | 8653.2875 | H2O | 70297.3753 | H2O | 59198.4097
moles | 237.0353 |  | O2 | 2016.3 |  | in total | 9653.2875 | O2 (fuel+air) | none | O2 (fuel+air) | 33156.0426
|  |  | sum | 8653.2875 |  | ash(-) | 9553.3875 | N2(fuel+air) | 741970.6636 | N2(fuel+air) | 749553.8194
|  |  | diff | 0 |  | diff | 0 | SO2 | 2450.6446 | SO2 | 2063.7223
[8 empty] | Ash | none | Ash | none |  |  | From Boiler
[6 empty] | consistency check |  | Water | 19301.4028 | Water | 16253.9831
[6 empty] | air (x 1.2) | 11249.2738 | [6 empty] | here the new basis is:
[6 empty] | in total | 12249.2738 |  | As |  | As |  |  | 47.1805 | kg/s | or | 374455 | lb/hr
|  | consistency checks |  |  |  | ash (-) | 12149.3738 |  | g/s |  | g/s |  |  |  | kg/s |  | lb/hr
|  |  | C | 637.5 |  | diff | 865.3287 | CO2 | 2337.5 | CO2 | 2337.5 | Theoretical Air |  | CO2 | 110.2845 |  | 875288.5625
| In Coal |  | H | 45 |  |  |  | H2O | 405 | H2O | 405 |  |  | H2O | 19.1081 |  | 151654.275
| diff-O | -68.8 | O2 | 2085.1 |  |  |  | O2 (fuel+air) | none | O2 (fuel+air) | 403.26 |  |  | O2 (fuel+air) | none |  | none
| diff - ash | -12.5 | N2 | 6649.4875 |  |  |  | N2(fuel+air) | 6649.4875 | N2(fuel+air) | 7976.885 |  |  | N2(fuel+air) | 313.7263 |  | 2489933.8418
|  |  | S | 25.1 |  |  |  | SO2 | 50.2 | SO2 | 50.2 |  |  | SO2 | 2.3685 |  | 18797.641
[8 empty] | Ash | none | Ash | none |  |  | Ash | 4.7133 |  | 37408.0545
|  | these values are right | [5 empty] | Water | 111.2 | Water | 111.2 |  |  | Water | 5.2465 |  | 41639.396
|  | in grams/s IN | [5 empty] | Total (g/s) | 9553.3875 | Total (g/s) | 11284.045 |  |  | Total Gas | 450.7339 |  | 3577313.7163
[14 empty] | Total Water | 24.3546 |  | 193293.671
[9 empty] | As |  | As
[9 empty] | wt% |  | wt% |  |  |  | kg/s |  | lb/hr |  | DOE Report
[8 empty] | CO2 | 24.4678 | CO2 | 20.7151 | 1.2 x Air |  | CO2 | 110.2845 |  | 875288.5625 |  | 867210
[8 empty] | H2O | 4.2393 | H2O | 3.5891 |  |  | H2O | 19.1081 |  | 151654.275
[8 empty] | O2 (fuel+air) | none | O2 (fuel+air) | 3.5737 |  |  | O2 (fuel+air) | 19.026 |  | 151002.7233 |  | 144807
[8 empty] | N2(fuel+air) | 69.6035 | N2(fuel+air) | 70.6917 |  |  | N2(fuel+air) | 376.3536 |  | 2986984.4727 |  | 2942220
[8 empty] | SO2 | 0.52547 | SO2 | 0.44488 |  |  | SO2 | 2.3685 |  | 18797.641 |  | 20202
[8 empty] | Ash | none | Ash | none |  |  | Ash | 4.7133 |  | 37408.0545 |  | 33851
[8 empty] | Water | 1.164 | Water | 0.98546 |  |  | Water | 5.2465 |  | 41639.396
[8 empty] | Total | 100 | Total | 100 |  |  | Total Gas | 532.3872 |  | 4225367.0705 |  | 4205743
[14 empty] | Total Water | 24.3546 |  | 193293.671 |  | 231294
[8 empty] | OUT GAS | Stack | OUT GAS | Stack |  |  | At Stack
[9 empty] | Exit with |  | Exit with
[9 empty] | Theoretical |  | 1.2 x | [6 empty] | (ESP) +
[9 empty] | Air |  | Air | [6 empty] | w 95% SO2
[9 empty] | Moles/s |  | Moles/s |  |  |  | kg/s |  | lb/hr | Removal
[8 empty] | CO2 | 53.125 | CO2 | 53.125 | Theoretical Air |  | CO2 | 110.2845 |  | 875288.5625
[8 empty] | H2O | 22.5 | H2O | 22.5 |  |  | H2O | 19.1081 |  | 151654.275
[8 empty] | O2 (fuel+air) | none | O2 (fuel+air) | 12.6019 |  |  | O2 (fuel+air) | none |  | none
[8 empty] | N2(fuel+air) | 237.4817 | N2(fuel+air) | 284.8888 |  |  | N2(fuel+air) | 313.7263 |  | 2489933.8418
[8 empty] | SO2 | 0.039219 | SO2 | 0.039219 |  |  | SO2 | 0.11842 |  | 939.8821
[8 empty] | Ash | none | Ash | none |  |  | Ash | 0 |  | 0
[8 empty] | Water | 6.1778 | Water | 6.1778 |  |  | Water | 5.2465 |  | 41639.396
[6 empty] | includes FGD |  | Total Water | 56.9937 | Total Water | 56.9937 |  |  | Total Water | 48.4019 |  | 384148.4698
[8 empty] | Total (mol/s) | 376.3174 | Total (mol/s) | 436.3263 |  |  | Total Gas | 472.5311 |  | 3750310.7561
(ESP) +
[9 empty] | As |  | As | [6 empty] | w 95% SO2
[9 empty] | ppm |  | ppm |  |  |  | kg/s |  | lb/hr | Removal | DOE Report
[8 empty] | CO2 | 141170.7214 | CO2 | 121755.1991 | 1.2 x Air |  | CO2 | 110.2845 |  | 875288.5625 |  | 866156 | lb/hr
[8 empty] | H2O | 59789.9526 | H2O | 51566.9078 |  |  | H2O | 19.1081 |  | 151654.275
[8 empty] | O2 (fuel+air) | none | O2 (fuel+air) | 28881.7656 |  |  | O2 (fuel+air) | 19.026 |  | 151002.7233 |  | 144587 | lb/hr
[8 empty] | N2(fuel+air) | 631067.5277 | N2(fuel+air) | 652925.863 |  |  | N2(fuel+air) | 376.3536 |  | 2986984.4727 |  | 2942220 | lb/hr
[8 empty] | SO2 | 104.2172 | SO2 | 89.884 |  |  | SO2 | 0.11842 |  | 939.8821 |  | 1063 | lb/hr
[8 empty] | Ash | none | Ash | none |  |  | Ash | 0 |  | 0 |  | 0 | 33851(ESP)
[8 empty] | Water | 16416.4018 | Water | 14158.6177 |  |  | Water | 5.2465 |  | 41639.396
[6 empty] | includes FGD |  | Total Water | 151451.1793 | Total Water | 130621.7628 |  |  | Total Water | 48.4019 |  | 384148.4698 |  | 436024 | lb/hr
[14 empty] | Total Gas | 554.1845 |  | 4398364.1103 |  | 4205743 | lb/hr
Total Water includes 38 mole H2O / mole SO2 removed (FGD)
100% electrostaic percipitator (ESP)