## Sheet1
13
Data Reconciliation Solution
Data | [9 empty] | Units Used in Figure Above
lb/s
TRef | 536.67 | R | [7 empty] | deg F
PRef | 14.696 | psia | [7 empty] | psia
MWAir | 28.965 | lbs/mol | [7 empty] | LHV
MWWater | 18.0153 | lbs/mol | [7 empty] | Btu/s
MWMethane | 16.043 | lbs/lb-mol | [7 empty] | MW
1 hr = | 3600 s
1 Btu/hr = | 0.29307 W
1000 W = | 1 kW
Pressure Data |  |  |  | Theoretical Air Required |  |  |  | Parameters determined after data reconciliation
P0 | 14.696 | psia | [5 empty] | QAir Cooler |  | #NAME? | Btu/s |  |  |  |  | Turbine Efficiency Calculations
P1 | 14.696 | psia |  | CH4 | 9.5465 |  | mole air/mole fuel | Net Power |  | 19269.9319 | kW
P2 | 243.7 | psia |  | DAR | 3.4326 |  |  | Rate Heat Addition |  | 199408306.2891 | Btu/hr |  |  |  | Compressor |  | Gas Generating Turbine |  | Power Turbine
P3 | 243.7 | psia |  | CH4 H/C | 4 |  |  | Heat Rate |  | 10348.1583 | Btu/kW-hr |  |  | sAir,1 | #NAME? | sProd,3 | #NAME? | sProd,4 | #NAME? | Btu/lb-R
P4 | 56.9 | psia | [11 empty] | s2, isen | #NAME? | s4, isen | #NAME? | s5, isen | #NAME? | Btu/lb-R
P5 | 14.82 | psia | [5 empty] | Economizer |  |  | Evaporator |  |  | T2, isen | #NAME? | T4, isen | #NAME? | T5, isen | #NAME? | R
P6 | 14.82 | psia | [5 empty] | AEcon | 10565 | ft2 | AEvap | 56248 | ft2 | h2, isen | #NAME? | h4, isen | #NAME? | h5, isen | #NAME? | Btu/lb
P7 | 14.82 | psia | [5 empty] | ΔTLMTD | 109.4808 | R | ΔTLMTD | 264.1386 | R | ηCompressor | #NAME? | ηGas Turbine | #NAME? | η Power Turbine | #NAME?
PCWa | 60 | psia | [5 empty] | QEcon | #NAME? | Btu/s | Qevap | #NAME? | Btu/s
PCWb | 60 | psia | [5 empty] | UEcon | #NAME? | Btu/hr-ft2-R | UEvap | #NAME? | Btu/hr-ft2-R
PEcon | 239 | psia
PEvap | 198 | psia | [5 empty] | ΔTPinch | 55.8923 | R
PSteam | 140.9 | psia | [5 empty] | ΔTApproach | 32.3014 | R
Data Reconciliation Problem
These two cells are only used in the figure above and with the Macro - Write Data Recon Values
| 19.27 | 19.27
Variables | Measured | Reconciled | St. Dev | OBJ |  | hReconciled |  | Material Balances (lb/s)
FAir | 145 | 152.7237 | 20 | 0.14914 | [5 empty] | IN | OUT | DIFF
FNG | 2.6208 | 2.5814 | 0.07 | 0.31698 |  |  |  | Combustion Chamber |  | 155.305 | 155.305 | 0
FProd | 147.6208 | 155.305 | 20 | 0.14762 |  |  |  | HRSG |  | 24.5659 | 24.5659 | 0
FWater, Econ | 24.4444 | 24.5659 | 1.2222 | 0.0098781
FSteam | 24.17 | 24.2859 | 0.725 | 0.025538
FBlowdown | 0.28 | 0.28001 | 0.1 | 1.6492e-08 |  |  |  | Energy Balances (Btu/s)
FCW | 200 | 193.9783 | 44 | 0.01873 | [5 empty] | IN | OUT | DIFF
T0 | 547.17 | 547.2477 | 2 | 0.0015086 |  | #NAME? | hAir,0 | Air Cooler |  | #NAME? | #NAME? | #NAME?
T1 | 519.94 | 519.0908 | 5 | 0.028846 |  | #NAME? | hAir,1 | Compressor/GGT |  | #NAME? | #NAME? | #NAME?
T2 | 1260.48 | 1260.1653 | 10 | 0.00099032 |  | #NAME? | hAir,2 | Combustion |  | #NAME? | #NAME? | #NAME?
T3 | 2400 | 2446.6485 | 150 | 0.096715 |  | #NAME? | hProd,3 | Power Turbine |  | #NAME? | #NAME? | #NAME?
T4 | 1836.34 | 1833.7712 | 30 | 0.0073318 |  | #NAME? | hProd,4 | Evap |  | #NAME? | #NAME? | #NAME?
T5 | 1386.67 | 1412.0585 | 60 | 0.17905 |  | #NAME? | hProd,5 | Eco |  | #NAME? | #NAME? | #NAME?
T6 | 914.67 | 877.5671 | 50 | 0.55065 |  | #NAME? | hProd,6
T7 | 787.67 | 797.6416 | 20 | 0.24858 |  | #NAME? | hProd,7
TCWa | 504.57 | 507.1745 | 5 | 0.27134 |  | #NAME? | hCW,a
TCWb | 515.07 | 512.4828 | 5 | 0.26775 |  | #NAME? | hCW,b
LHV | 21501 | 21457.8996 | 200 | 0.046441
TWater, Econ | 677.67 | 663.6964 | 30 | 0.21696 |  | #NAME? | hWater, Econ
TWater, Evap | 780.67 | 789.3733 | 30 | 0.084165 |  | #NAME? | hWater, Evap
TSteam | 821.67 | 821.6748 | 1 | 2.2912e-05 |  | #NAME? | hWater,BlowD
WNet | 18264.44 | 18264.4381 | 0.01 | 0.036918 |  | #NAME? | hSteam
QCC,loss | 1125 | 1344.4412 | 1000 | 0.048154 |  |  |  | Chiinv (0.05,8)
|  |  |  | 2.7533 | ΣOBJ |  |  | 15.5073