## WB! Status
What'sBest!® 8.0.4.1 (May 08, 2006) - Library 4.1.1.41 - Status Report -
DATE GENERATED: | 2008-11-19 16:55 | 39771.7051
MODEL INFORMATION:
CLASSIFICATION DATA Current Capacity Limits
--------------------------------------------------------
Numerics 27
Variables 77
Adjustables 26 500
Constraints 25 250
Integers/Binaries 0/14 50
Nonlinears 24 50
Coefficients 176
Minimum coefficient value: 1 on Costs!J16
Minimum coefficient in formula: Costs!J16
Maximum coefficient value: 45000 on Costs!B44
Maximum coefficient in formula: Costs!J17
MODEL TYPE: Mixed Integer / Nonlinear
SOLUTION STATUS: LOCALLY OPTIMAL
OPTIMALITY CONDITION: SATISFIED
OBJECTIVE VALUE: 1548109.3947037
DIRECTION: Minimize
SOLVER TYPE: Branch-and-Bound
TRIES: 9732
INFEASIBILITY: 0
BEST OBJECTIVE BOUND: 1548109.3947037
STEPS: 19
ACTIVE: 0
SOLUTION TIME: 0 Hours 0 Minutes 32 Seconds
ERROR / WARNING MESSAGES:
***WARNING***
Nonlinearities Present (Help Reference: NLINCELL):
The cells below contain nonlinear expressions. If these cells are used only for
reporting, then, for efficiency, they should be included in a WBOMIT range (refer
to documentation). In some cases, nonlinear cells may be linearized automatically
by the Linearization option that is set in the General Options dialog box. This
warning can be turned off with the Nonlinearity Present checkbox in the
General Options dialog box
(cell addresses listed at bottom of tab).
LISTING:
***WARNING***
List of nonlinear cells:
Costs!J16 | Costs!B25 | Costs!G25 | Costs!B26
Costs!G26 | Costs!B27 | Costs!B28 | Costs!B34
Costs!E34 | Costs!B35 | Costs!E35 | Costs!B36
End of Report

## Costs
Utility Superstructure
FIXED
Steam | [5 empty] | HP Boiler |  | 90000 | $/yr
ΔH (HP to MP) |  |  | 71 | kW-hr/ton |  | MP Boiler |  | 40000 | $/yr
ΔH (MP to LP) |  |  | 112 | kW-hr/ton |  | HP Turbine |  | 45000 | $/yr
MP Demand |  |  | 25 | ton/hr |  | MP Turbine |  | 25000 | $/yr
LP Deamnd |  |  | 85 | ton/hr |  | Variable
[6 empty] | HP Boiler |  | 9600 | $hr/yr-ton
ELECTRICITY | [5 empty] | MP Boiler |  | 8500 | $hr/yr-ton
Power A Demand |  |  | 7500 | kW |  | HP Turbine |  | 25 | $/yr-kW
Power B Demand |  |  | 4500 | kW |  | MP Turbine |  | 14.5 | $/yr-kW
Other
Turbine Efficiency |  |  | 0.65 |  |  | HP Turbine Extraction |  | 20000 | $/yr
Costs
[6 empty] | Cost Boilers |  | 1205359.3947 | $/yr
[6 empty] | Cost HP Turbines |  | 252500 | $/yr
[6 empty] | Cost MP Turbines |  | 90250 | $/yr
[6 empty] | TOTAL COST |  | 1548109.3947 | $/yr
ELECTRICITY BALANCE |  |  |  |  | Turbine Steam Mass Balances
PRODUCED (kW) | [5 empty] | In-Out
Power 1 | 7500 |  |  |  | Turbine 1 | 0
Power 2 | 0 |  |  |  | Turbine 2 | 0
Power 3 | 0
Power 4 | 4500
Power 1 + 3 | 7500
Power 2 + 4 | 4500
Process Steam Mass Balances
PRODUCED (ton/hr) |  |  | USED (ton/hr) |  |  | Available to Process (ton/hr)
HP Steam | 116.1833 |  | HP Steam | 116.1833 |  | HP Steam | 0
MP Steam | 86.8132 |  | MP Steam | 61.8132 |  | MP Steam | 25
LP Steam | 91.1833 |  | LP Steam | 0 |  | LP Steam | 91.1833
EQUIPMENT SELECTION
NAME | ON/OFF | [5 empty] | ON/OFF
HP Bolier | 1 | 116.1833 | F1 ton/hr
HP Letdown | 0 | 0 | F11 ton/hr
Turbine 1 HP Feed | 1 | 116.1833 | F3 ton/hr
Turbine 1 HP to MP Only | 1 | 86.8132 | F5 ton/hr
Turbine 1 HP to MP to LP | 1 | 29.3701 | F6 ton/hr |  | Turbine Extraction
Turbine 2 HP Feed | 0 | 0 | F4 ton/hr |  | Constraint: | δ5+ δ6- δT1_Ext <=1 | 1
Turbine 2 HP to MP Only | 0 | 0 | F7 ton/hr |  | Constraint: | δ3 - δT1_Ext >=0 | 0
Turbine 2 HP to MP to LP | 0 | 29.5685 | F8 ton/hr |  | Constraint: | δ7 + δ8 - δT2_Ext <=1 | 0
MP Boiler | 0 | 130 | F2 ton/hr |  | Constraint: | δ4 - δT2_Ext >=0 | 0
MP Letdown | 0 | 82 | F12 ton/hr
Turbine 3 MP to LP | 0 | 0 | F9 ton/hr |  | Turbine Usage Constraints
Turbine 4 MP to LP | 1 | 61.8132 | F10 ton/hr |  | Constraint: | for Power A: δ3+ δ9 = 1 | 1
Turb 1 Extract (F5 and F6) | 1 |  |  |  | Constraint: | for Power B: δ4 + δT10 = 1 | 1
Turb 2 Extract (F7 and F8) | 0
CONSTRAINTS WB
NAME |  |  | CONSTRAINT |  |  |  | MAX STEAM FLOW CONSTRAINT
HP Turbine 1 Mass Balance |  |  | #VALUE! |  |  | Steam Flow F1 | #VALUE! | Steam Flow Upper Bound
HP Turbine 2Mass Balance |  |  | #VALUE! |  |  | Steam Flow F2 | #VALUE! | 130
Extraction Used HP Turbine 1 |  |  | #VALUE! |  |  | Steam Flow F3 | #VALUE!
Extraction Used HP Turbine 1 |  |  | #VALUE! |  |  | Steam Flow F4 | #VALUE!
Extraction Used HP Turbine 2 |  |  | #VALUE! |  |  | Steam Flow F5 | #VALUE!
Extraction Used HP Turbine 2 |  |  | #VALUE! |  |  | Steam Flow F6 | #VALUE!
One HP or MP Turbine for Power Demand A |  |  | #VALUE! |  |  | Steam Flow F7 | #VALUE!
One HP or MP Turbine for Power Demand B |  |  | #VALUE! |  |  | Steam Flow F8 | #VALUE!
Power Demand A |  |  | #VALUE! |  |  | Steam Flow F9 | #VALUE!
Power Demand B |  |  | #VALUE! |  |  | Steam Flow F10 | #VALUE!
Process HP Steam |  |  | #VALUE! |  |  | Steam Flow F11 | #VALUE!
Process MP Steam |  |  | #VALUE! |  |  | Steam Flow F12 | #VALUE!
Process LP Steam |  |  | #VALUE!