## Sheet1
Cogeneration Cost Comparison
| Current Plant | [5 empty] | Cogeneration
| kW | 1000 | kw |  |  |  | Installed Cost | 1100 | $/kW | 1100000 | $ total investment
| Steam | 4800 | lb/hr |  |  |  | CRF | 0.16 | yr-1
| Electricty | 0.07 | $/kw-hr |  |  |  | NG cost | 8e-06 | $/Btu
| Demand | 7 | $/kw-month |  |  |  | O&M cost | 0.005 | $/kW-hr
| Steam cost | 0.009 | $/lb |  |  |  | Heat Rate | 10316 | Btu/kW-hr
| hr/yr | 8000 | hours
| month/yr | 12 | mo/yr
|  |  | Costs |  |  |  |  | Costs
| Electricity Cost |  | 70 | $/hr |  |  | Capital | 22 | $/hr
| Demand |  | 10.5 | $/hr |  |  | Natural Gas | 82.528 | $/hr
| Steam |  | 43.2 | $/hr
[9 empty] | useable heat = | 4920732 | Btu/hr
[9 empty] | steam generated = | 4920.732 | lb/hr
[7 empty] | O&M | 5 | $/hr
|  |  | ________ |  |  |  |  | ________
| total |  | 123.7 | $/hr |  |  | total | 109.528 | $/hr
|  |  | 989600 | $/yr |  |  |  | 876224 | $/yr
savings
[5 empty] | 14.172 | $/hr
[5 empty] | 113376 | $/yr