## WB! Status
What'sBest!® 8.0.4.4 (Aug 23, 2006) - Library 4.1.1.93 - Status Report -
DATE GENERATED: | 2008-02-24 20:36 | 39502.8585
MODEL INFORMATION:
CLASSIFICATION DATA Current Capacity Limits
--------------------------------------------------------
Numerics 178
Variables 137
Adjustables 32 500
Constraints 44 250
Integers/Binaries 0/16 50
Nonlinears 44 50
Coefficients 278
Minimum coefficient value: 0.084303943622806 on Costs!D12
Minimum coefficient in formula: Costs!D13
Maximum coefficient value: 26250 on <RHS>
Maximum coefficient in formula: Costs!D77
MODEL TYPE: Mixed Integer / Nonlinear
SOLUTION STATUS: LOCALLY OPTIMAL
OPTIMALITY CONDITION: SATISFIED
OBJECTIVE VALUE: 2581.3744394228
DIRECTION: Minimize
SOLVER TYPE: Branch-and-Bound
TRIES: 4779
INFEASIBILITY: 1.3371756040215e-005
BEST OBJECTIVE BOUND: 2581.3744394228
STEPS: 4
ACTIVE: 0
SOLUTION TIME: 0 Hours 0 Minutes 45 Seconds
NON-DEFAULT SETTINGS:
General Options / Warning Nonlinearity Present: Off
End of Report

## Costs
Process Energy Dispatch Optimization
Predicted
NATURAL GAS | [6 empty] | INPUTS
LSU NG Price (HHV) |  |  | 9.59 | $/MMBTU |  |  | Henry Hub (NYMEX) Price |  |  | 9.41 | $/MMBTU
NG Purchased (HHV) |  |  | 193.3017 | MMBTU/hr |  |  | Natural Gas (HHV) |  |  | 1054.8677 | BTU/SCF
NG flow rate (based on NG_HHV) |  |  | 183.2473 | mSCF/hr |  |  | Campus Electricity Demand |  |  | 23735 | kW
NG Cost |  |  | 1853.763 | $/hr |  |  | Campus Steam Demand |  |  | 40.731 | mlb/hr
[7 empty] | Campus CHW Demand |  |  | 3526 | tons
VARIABLE ELECTRICITY | [6 empty] | Ambient Air Temperature |  |  | 33 | deg F
Base Rate |  |  | 0.01034 | $/kW-hr |  |  | Relative Humidity |  |  | 33 | %
Fuel Adjustment |  |  | 0.073964 | $/kW-hr |  |  | Electricity Base Rate |  |  | 0.01034 | $/kW-hr
Electricity Purchased |  |  | 6984.277 | kW |  |  | May-Oct Demand Rate |  |  | 6.49 | $/kW
Variable Electricity Cost |  |  | 588.8021 | $/hr |  |  | Nov-Apr Demand Rate |  |  | 5.67 | $/kW
[7 empty] | Contract Power |  |  | 17500 | kW
FIXED ELECTRICITY | [6 empty] | Prior Monthly Average NYMEX |  |  | 13.157 | $/MMBTU
Facilities Charge |  |  | 35.45 | $/hr |  |  | Prior Monthly Average Spot Market |  |  | 0.09897 | $/kW-hr
Demand Rate |  |  | 5.67 | $/kW-month |  |  | Predicted Fuel Adjustment |  |  | 0.073964 | $/kW-hr
Demand Billing Load |  |  | 13125 | kW |  |  | Peak Period |  |  | 0 | 0 or 1
Demand Charge |  |  | 103.3594 | $/hr |  |  | Off Peak Period |  |  | 1 | 0 or 1
Fixed Electricity Cost |  |  | 138.8094 | $/hr |  |  | May-Oct |  |  | 0 | 0 or 1
[7 empty] | Nov-Apr |  |  | 1 | 0 or 1
TOTAL COST |  |  | 2581.3744 | $/hr
ELECTRICITY BALANCE | [5 empty] | STEAM BALANCE
PRODUCED (kW) |  |  | USED (kW) |  |  | PRODUCED (mlb/hr) |  |  | USED (mlb/hr)
GE Gas Turbine | 16750.723 |  | Campus | 23735 |  | Boiler 8 | 78.4554 |  | Campus | 40.731
Imported | 6984.277 |  | Chiller 1 | 0 |  | Boiler 8 Supp. | 0 |  | Chiller 8 | 0
SUM | 23735 |  | Chiller 2 | 0 |  | Boiler 7 | 0 |  | Chiller 9 | 14.6219
|  |  | Chiller 3 | 0 |  | Boiler 7 Supp. | 0 |  | Chiller 10 | 23.1025
MAX IMPORTED (kW) |  |  | Chiller 4 | 0 |  | Boiler 4 | 0 |  | SUM | 78.4554
| 26250 |  | Chiller 5 | 0 |  | SUM | 78.4554
|  |  | Chiller 7 | 0
|  |  | SUM | 23735
CHILLED WATER BALANCE | [5 empty] | NATURAL GAS
PRODUCED (tons) |  |  | USED (tons) |  |  | PURCHASED (MMBTU/hr) |  |  | USED (MMBTU/hr)
Chiller 1 | 0 |  | Campus | 3526 |  | SUM | 193.3017 |  | GE G T | 193.3017
Chiller 2 | 0 |  | Air Cooler | -175.8111 | -202.2527 |  |  |  | Boiler 8 Supp. | 0
Chiller 3 | 0 |  | SUM | 3350.1889 |  |  |  |  | Allison G T | 0
Chiller 4 | 0 | [7 empty] | Boiler 7 Supp. | 0
Chiller 5 | 0 | [7 empty] | Boiler 4 | 0
Allison Chiller | 0 | [7 empty] | SUM | 193.3017
Chiller 7 | 0
Chiller 8 | 0
Chiller 9 | 1290.189
Chiller 10 | 2060
SUM | 3350.189
EQUIPMENT SELECTION
NAME | ON/OFF | IN |  | OUT |  | EFFICIENCY |  | MAX CAPACITY |  | MIN CAPACITY
Chiller 1 | 0 | 206.8815 | kW | 320.25 | tons | 544.4045 | % | 1600 | tons | 320 | tons
Chiller 2 | 0 | 276 | kW | 400 | tons | 509.6888 | % | 2000 | tons | 400 | tons
Chiller 3 | 0 | 120.8 | kW | 200 | tons | 582.2604 | % | 1000 | tons | 200 | tons
Chiller 4 | 0 | 215.9 | kW | 340 | tons | 553.8351 | % | 1700 | tons | 340 | tons
Chiller 5 | 0 | 262 | kW | 400 | tons | 536.9241 | % | 2000 | tons | 400 | tons
Chiller 7 | 0 | 138.6 | kW | 220 | tons | 558.2306 | % | 1100 | tons | 220 | tons
Chiller 8 | 0 | 5.6984 | mlb/hr | 500 | tons | 93.5385 | % | 2060 | tons | 500 | tons
Chiller 9 | 1 | 14.6219 | mlb/hr | 1290.189 | tons | 94.0642 | % | 2060 | tons | 500 | tons
Chiller 10 | 1 | 23.1025 | mlb/hr | 2060 | tons | 95.0567 | % | 2060 | tons | 500 | tons
Boiler 4 | 0 | 23.4023 | MMBTU/hr | 20 | mlb/hr | 85.9145 | % | 100 | mlb/hr | 20 | mlb/hr
GE Gas Turbine | 1 | 193.3017 | MMBTU/hr | 16750.723 | kW | 29.5682 | % | 20100 | kW | 4000 | kW
Boiler 8 | 1 | 193.3017 | MMBTU/hr | 78.4554 | mlb/hr | 40.94 | % | 89.57 | mlb/hr | 36.2 | mlb/hr
Boiler 8 Supp. | 0 | 0.25758 | MMBTU/hr | 0.25 | mlb/hr | 97.9027 | % | 60.43 | mlb/hr | 0 | mlb/hr
Allison G T/Chill | 0 | 20.6001 | MMBTU/hr | 2917.8811 | tons | 169.9732 | % | 6400 | tons | 2500 | tons
Boiler 7 | 0 | 20.6001 | MMBTU/hr | 16.6 | mlb/hr | 81.0094 | % | 22 | mlb/hr | 16.6 | mlb/hr
Boiler 7 Supp. | 0 | 0.2 | MMBTU/hr | 0.19477 | mlb/hr | 97.9018 | % | 71.5 | mlb/hr | 0 | mlb/hr
CONSTRAINTS
NAME |  |  | CONSTRAINT
GE Gas Turbine = Boiler 8 binary |  |  | #VALUE!
GE Gas Turbine = Boiler 8 mcf/hr |  |  | #VALUE!
Boiler 8 Supp <= Boiler 8 binary |  |  | #VALUE!
Allison Gas Tur = Boiler 7 binary |  |  | #VALUE!
Allison Gas Tur = Boiler 7 mcf/hr |  |  | #VALUE!
Boiler 7 Supp <= Boiler 7 binary |  |  | #VALUE!
Electricity Imported >= 0 |  |  | #VALUE!
Electricity Imported <= Max Electricity |  |  | #VALUE!
Electricity Produced = Consumed |  |  | #VALUE!
Steam Produced = Consumed |  |  | #VALUE!
Chilled Water Produced = Consumed |  |  | #VALUE!
Natural Gas Purchased = Used |  |  | #VALUE!
Equipment Capacity |  |  | MAX | MIN
| Chiller 1 |  | #VALUE! | #VALUE!
| Chiller 2 |  | #VALUE! | #VALUE!
| Chiller 3 |  | #VALUE! | #VALUE!
| Chiller 4 |  | #VALUE! | #VALUE!
| Chiller 5 |  | #VALUE! | #VALUE!
| Chiller 7 |  | #VALUE! | #VALUE!
| Chiller 8 |  | #VALUE! | #VALUE!
| Chiller 9 |  | #VALUE! | #VALUE!
| Chiller 10 |  | #VALUE! | #VALUE!
| Boiler 4 |  | #VALUE! | #VALUE!
| GE Gas Turbine |  | #VALUE! | #VALUE!
| Boiler 8 |  | #VALUE! | #VALUE!
| Boiler 8 Supp. |  | #VALUE! | #VALUE!
| Allison GT/Chill |  | #VALUE! | #VALUE!
| Boiler 7 |  | #VALUE! | #VALUE!
| Boiler 7 Supp. |  | #VALUE! | #VALUE!