## English
Air Standard Cycle with HRSG Supplemental Firing
Fuel
Overall Energy Balance Method |  |  |  | 3.7745 | lb/s
Heat Rate (BTU/kW-hr) |  | 1237.3837 | T2 ( R) | 2520 | T3 ( R) |  | Gas (Air + Fuel)
9157.2177 |  | 15.9 | P2 (atm) | 15.9 | P3 (atm) |  | 203.7745 | lb/s
[7 empty] | 1385.5447 | T5 ( R)
|  |  | 81151.3406 | Q (BTU/s) |  |  | 1 | P5 (atm)
Air Feed
200 | lb/s
519 | T1 ( R) |  | -34482.4178 |  |  |  | 30246.0348 | W_PT (BTU/s)
1 | P1 (atm) |  | W_AC (BTU/s) |  | 1915.6481 | T4 ( R) |  | 31.9032 | MW
[5 empty] | 4.4857 | P4 (atm)
Supplemental Firing
[7 empty] | 203.7745 | lb/s | 205.0829 | lb/s
Stack | 203.7745 | lb/s |  |  |  |  | 1385.5447 | T6( R) | 1870 | T6_SF ( R)
| #NAME? | T7( R) |  |  |  |  | 1 | P6 (atm)
| 1 | P7 (atm)
[7 empty] | #NAME? | lb/s | #NAME? | lb/s
[7 empty] | 874 | T9( R)
[7 empty] | 290 | P9 (psia)
| #NAME? | lb/s
| 700 | T8( R) | Economizer |  | Evaporator
| 290 | P8 (psia) | #NAME? |  | 28331.2774
Variables |  |  | Physical |  |  | Units Conversion
Fair (lb/s) = | 200 | γa = | 1.4 |  |  | 3600 s = 1 hr | 3600
nAC = | 0.87 | Cp,a (BTU/lb-R) = | 0.24 |  |  | 3.413 BTU/hr= W | 3.413
P2 (atm) = | 15.9 | γg = | 1.33 |  |  | 1000 W = kW | 1000
T3 (R) = | 2520 | Cp,g (BTU/lb-R) = | 0.28
nGT = | 0.89 | Tref (R) = | 536.67
nPT = | 0.89 | CH4(BTU/lb) = | 21500 |  |  | Sheet Functions Used Here
Design ΔTpinch ( R) = | 15 | hv,sat(874R, P9) = | #NAME? | BTU/lb |  | MW H20 | 18.0153
Design ΔTapproach ( R) = | 15 | hl(T8P, 290) = | #NAME? | BTU/lb
|  | hl(700 R, 290) = | #NAME? | BTU/lb
[8 empty] | blue | variable
[8 empty] | plum | constant
|  | Material and Energy Balances | [5 empty] | teal | calculated
Temperatures (Real) |  | Isentropic_Temps |  | Pressures |  | Air_Fuel_Steam
T0 (R) = | 519 |  |  | P0 (atm) = | 1
T1 (R) = | 519 |  |  | P1 (atm) = | 1
T2 (R) = | 1237.3837 |  |  | P2 (atm) = | 15.9 | nCC = | 0.98
T3 (R) = | 2520 |  |  | P3 (atm) = | 15.9 | Ffuel(lb/s) = | 3.7745
T4 (R) = | 1915.6481 | T4_Iso (R) = | 1840.9529 | P4 (atm) = | 4.4857
T5 (R) = | 1385.5447 | T5_Iso (R) = | 1320.0263 | P5 (atm) = | 1 | Fair + Ffuel (lb/s) = | 203.7745
T6 (R) = | 1385.5447 |  |  | P6 (atm) = | 1
T7p(R) = | 889 |  |  | P7p (atm) = | 1 | Fsteam(lb/s) = | #NAME?
T7 (R) = | #NAME? |  |  | P7 (atm) = | 1 | Fwater(lb/s) = | #NAME?
T8 (R) = | 700 |  |  | P8 (psia) = | 290
T8p (R) = | 859 |  |  | P8p (psia) = | 290
T9 (R) = | 874 |  |  | P9 (psia) = | 290
T6_SF (R) = | 1870 |  | Supplemental | Firing |  | FFuel_SF(lb/s) = | 1.3084
T7p_SF ( R) = | #NAME? |  |  |  |  | FFuel_SF + Fgas(lb/s) = | 205.0829
ΔTpinch_SF ( R) = | #NAME? |  |  |  |  | FSteam_SF(lb/s) = | #NAME?
[6 empty] | FWater_SF(lb/s) = | #NAME?
| Heat |  |  |  | Work
QCC (BTU/s) = | 81151.3406 |  |  |  | WAC_Actual (BTU/s) = | -34482.4178
QLoss (BTU/s) = | 1623.0268 |  |  |  | WGT_Actual (BTU/s) = | 34482.4178
[5 empty] | WGT_Isentropic (BTU/s) = | 38744.2896
Efficiency = | 0.37271
| Design | Sup Firing |  |  | WPT_Actual (BTU/s) = | 30246.0348
Transferred QEvap (BTU/s) = | 28331.2774 | #NAME? |  |  | W_PT_Isentropic (BTU/s) = | 33984.3088
Transferred QEcon (BTU/s) = | #NAME? | #NAME?
[5 empty] | Power_Actual (kW) = | 31903.2304
checks
Transferred QEvap (BTU/s) = |  | #NAME?
Transferred QEcon (BTU/s) = |  | #NAME?