## Calculation
C | temp,k | RH | term | vappress | edewp |  | estdewpt | este | edewp-este
30 | 303.15 | 70 | 1.6388 | 43.5356 | 30.4749 |  | 297.1518 | 30.4654 | 0.009565
[5 empty] | Calculated Dew Point, C |  | 24.0018
rd & cp constants
|  | rd | 287.04 | TLCL | PLCL | esurf | mixr | mixr1 | theta | thetae | esttheta | eguess | mixrguess1 | estthetae | diff
|  | cp | 1005 | 22.5825 | 696.8592 | 30.4654 | 25.9735 | 0.025973 | 327.8677 | 414.6454 | 322.5144 | 32.463 | 0.027753 | 414.6357 | 0.0097001
|  | press | 760 | [5 empty] | tguess | ktguess
[6 empty] | Calculated Wet-Bulb Temperature, C |  |  | 25.0503 | 298.2003

## Main
This Program calculates the Wet-Bulb Temperature and Dew Point from
given Dry-Bulb Temperature, Relative Humidity and Station Pressure
(Zero station pressure will be defaluted to 760 millibar)
Enter the following:
|  |  | Unit | To convert oF to oC
Dry-Bulb Temperature |  | 30 | oC | Enter oF = | 86
Relative Humidity |  | 70 | % | Calculated oC = | 30
Pressure |  | 760 | millibar
To convert oC to oF
|  |  |  | Enter oC = | 24
|  |  |  | Calculated oF = | 75.2
Click On Calculate to Get Results For Different Conditions
Results
Dew Point |  | 24.0018 | oC
Wet-Bulb Temperature |  | 25.0503 | oC